## Table 1
Equipment for cogeneration units (CGU)
Equipment of Municipal Enterprise “Kharkiv Heat Networks” |  | Equipment for connecting through gas distribution networks |  |  | Equipment for connecting through power distribution networks
No. | GGU capacity 50, kW | Gas meter size* | Metering unit* | Gas pressure regulating cabinet (GPRC)* | Equipment for connecting through power distribution networks | Equipment for connecting through power distribution networks (high-voltage transmission lines)
1 | 100 | Delta Compact G25 DN50 (1:160) min 0,25 max 40 | Gas metering cabinet | GPRC - 4/4 - 2L - 40x50 - 3/3 B/249-АР 1 1/2"x1 1/2" + OS/66- AP (Tartarini)
2 | 120 | Delta Compact G25 DN50 (1:160) min 0,25 max 40 | Gas metering cabinet | GPRC - 4/4 - 2L - 40x50 - 3/3 B/249-АР 1 1/2"x1 1/2" + OS/66- AP (Tartarini)
3 | 150 | Delta Compact G-40 DN50 (1:200) min 0,3 max 65 | Gas metering cabinet | GPRC - 4/4 - 2L - 40x50 - 3/3 B/249-АР 1 1/2"x1 1/2" + OS/66- AP (Tartarini)
4 | 220 | G-65 Delta SE G-65 DN50 (1:200) min 0.5 max 100 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP
5 | 200 | Delta Compact G-40 DN50 (1:200) min 0,3 max 65 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP
6 | 1000 | G-250 Delta2100 G-250 DN100 (1:160) min 2,5 max 400 | Gas metering cabinet | GPRC - 7/10 - 2L - 65x100 - 3/3 MBN-QA DN50х100 PN16 + OS/66-AP | Power cables “10 3х240 mm2” 1,65 km; power transformer - 6/0,4 кV 1 МВА | A total of 5 pcs. of 10 kV cells including: A relay protection and automation (RPA) panel with a microprocessor device and power direction - 1 pc. Vacuum switch 1 pc.; Surge arresters nonlinear - 3 pcs. Current transformer -3 pcs; Power cables “КВВГЕнг 4*2,5” -0,75km ; “КВВГЕнг 10*2,5”-0,75km; “ПВ-1 2,5” - 1,0km
7 | 1000 | G-250 Delta2100 G-250 DN100 (1:160) min 2,5 max 400 | Gas metering cabinet | GPRC - 7/10 - 2L - 65x100 - 3/3 MBN-QA DN50х100 PN16 + OS/66-AP | Power cables “10 3х240 mm2” 1,65 km; transformer substation consisting of: power transformer-10/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs.; power transformer ТМГ-6/0,4 кV 1 МВА
8 | 1000 | G-250 Delta2100 G-250 DN100 (1:160) min 2,5 max 400 | Gas metering cabinet | GPRC - 7/10 - 2L - 65x100 - 3/3 MBN-QA DN50х100 PN16 + OS/66-AP | Transformer substation consisting of: power transformer ТМГ-6/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs.; power cables “ААБл 10 3х240 mm2” 1,65 km; “ААБл 10 3х120 mm2” 2 km ; power transformer ТМГ-6/0,4 kV 1 МВА
9 | 6000 | FLOWSIC600 G1600 DN250 (1:50) min 50 max2500 | Gas metering cabinet | GPRC - 11/17 - 2L - 200x250 - 3/3 BFL DN100 PN16 + PS/79-2 + OS/80X-BPA | Power cable “АпвЕгаПу-15 1*500/70 mm2” 2,3 km.
10 | 1500 | S3F Delta G-400 DN150 (1:160) min 4 max 650 | Gas metering cabinet | GPRC - 2L - 100x125 - 3/3 MBN- QA DN65х100 PN16 + OS/66-AP | Transformer substation consisting of: power transformer ТМГ-6/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs.; power cables “ААБл 10 3х240 mm2” 1,65 km; “ААБл 10 3х120 mm2” 2 km ; power transformer ТМГ-6/0,4 kV 1 МВА | A total of 10 pcs. of 10 kV cells including: A relay protection and automation (RPA) panel with a microprocessor device and power direction - 1 pc. Vacuum switch 1 pc.; Surge arresters nonlinear - 3 pcs.; Current transformer -3 pcs; Power cables “КВВГЕнг 4*2,5” -1,5km ; “КВВГЕнг 10*2,5”-1,5km; “ПВ-1 2,5” - 2,0km
11 | 9000 | FLOWSIC600 G2500 DN300 (1:50) min 80 max 4000 | Gas metering cabinet | GPRC - 12/18 - 2L - 250x300 - 3/3 FL + MB5 DN150 PN16 + PS/79-2 + OS/80X-BPA | Transformer substation consisting of: power transformer ТМГ-6/10 кV 2.5 МВА - 1 pc.; vacuum switch cells - 4 pcs.; power cables “АпвЕгаПу-15 1*500/70 mm2” 6 km.; Outdoor switchgear consisting of: vacuum switch cells - 5 pcs; voltage transformer cell - 1 pc.; Surge arresters nonlinear - 5 pcs.; power transformers ТМГ-6/0,4 кV 1 МВА ; ТМГ-10/0,4 кV 1 МВА
12 | 1500 | S3F Delta G-400 DN150 (1:160) min 4 max 650 | Gas metering cabinet | GPRC - 2L - 100x125 - 3/3 MBN- QA DN65х100 PN16 + OS/66-AP | Power cables “ААБл 10 3х240 mm2” 1,65 km; transformer substation consisting of: power transformer-10/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs. | A total of 3 pcs. of 10 kV cells including: A relay protection and automation (RPA) panel with a microprocessor device and power direction - 1 pc. Vacuum switch 1 pc.; Surge arresters nonlinear - 3 pcs.; Current transformer -3 pcs; Power cables “КВВГЕнг 4*2,5” -0,45km ; “КВВГЕнг 10*2,5”-0,45km; “ПВ-1 2,5” - 0,6km
13 | 1500 | S3F Delta G-400 DN150 (1:160) min 4 max 650 | Gas metering cabinet | GPRC - 2L - 100x125 - 3/3 MBN- QA DN65х100 PN16 + OS/66-AP | Power cables “ААБл 10 3х240 mm2” 1,65 km
14 | 1500 | S3F Delta G-400 DN150 (1:160) min 4 max 650 | Gas metering cabinet | GPRC - 2L - 100x125 - 3/3 MBN- QA DN65х100 PN16 + OS/66-AP | Power cables “ААБл 10 3х240 mm2” 1,65 km
15 | 1500 | S3F Delta G-400 DN150 (1:160) min 4 max 650 | Gas metering cabinet | GPRC - 2L - 100x125 - 3/3 MBN- QA DN65х100 PN16 + OS/66-AP | Transformer substation consisting of: power transformer ТМГ-6/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs.; power cables “ААБл 10 3х240 mm2” 1,65 km; “ААБл 10 3х120 mm2” 2 km;
16 | 11000 | FLOWSIC600 G2500 DN300 (1:50) min 80 max 4000 | Gas metering cabinet | GPRC - 12/18 - 2L - 250x300 - 3/3 FL + MB5 DN150 PN16 + PS/79-2 + OS/80X-BPA | Transformer substation consisting of: power transformer ТМГ-6/10 кV 2.5 МВА - 1 pc.; vacuum switch cells - 4 pcs.; power cables “АпвЕгаПу-15 1*500/70 mm2” 2.3 km.; Outdoor switchgear consisting of: vacuum switch cells - 5 pcs; voltage transformer cell - 1 pc.; Surge arresters nonlinear - 5 pcs.; power transformer ТМГ-10/0,4 кV 1 МВА;
17 | 3500 | FLOWSIC600 G1000 DN200 (1:30) min 50 max 1600 | Gas metering cabinet | GPRC - 10/16 - 2L - 150x200 - 3/3 MBN-QA DN100х200 PN16 + OS/66-AP | Power cables “ААБл 10 3х240 mm2” 1,65 km; transformer substation consisting of: power transformer-10/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs.; power transformer ТМГ-10/0,4 кV 1 МВА
18 | 250 | G-65 Delta SE G-65 DN50 (1:200) min 0.5 max 100 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP | Power cables “ААБл 10 3х240 mm2” 1,65 km | A total of 7 pcs. of 10 kV cells including: A relay protection and automation (RPA) panel with a microprocessor device and power direction - 1 pc. Vacuum switch 1 pc.; Surge arresters nonlinear - 3 pcs. Current transformer -3 pcs; Power cables “КВВГЕнг 4*2,5” 1,05km ; “КВВГЕнг 10*2,5”-1,05km; “ПВ-1 2,5” - 1,4km
19 | 250 | G-65 Delta SE G-65 DN50 (1:200) min 0.5 max 100 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP | Power cables “ААБл 10 3х240 mm2” 1,65 km
20 | 250 | G-65 Delta SE G-65 DN50 (1:200) min 0.5 max 100 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP | Power cables “ААБл 10 3х240 mm2” 1,65 km
21 | 3000 | TZ/FLUXI G650 DN200 (1:20) min 50 max 1000 (G- 650 Delta only D200 S3F Delta G-650 DN150 (1:200) min 5 max 1000 ) | Gas metering cabinet | GPRC - 10/16 - 2L - 150x200 - 3/3 MBN-QA DN100х200 PN16 + OS/66-AP | Transformer substation consisting of: power transformer ТМГ-6/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs.; power cables “АпвЕгаПу-15 1*500/70 mm2” 2,3 km.; “ААБл 10 3х120 mm2” 2 km;
22 | 8000 | FLOWSIC600 G2500 DN300 (1:50) min 80 max 4000 | Gas metering cabinet | GPRC - 12/18 - 2L - 250x300 - 3/3 FL + MB5 DN150 PN16 + PS/79-2 + OS/80X-BPA | Transformer substation consisting of: power transformer ТМГ-6/10 кV 2.5 МВА - 1 pc.; vacuum switch cells - 4 pcs.; power cables “АпвЕгаПу-15 1*500/70 mm2” 6 km.; Outdoor switchgear consisting of: vacuum switch cells - 5 pcs; voltage transformer cell - 1 pc.; Surge arresters nonlinear - 5 pcs.; power transformers ТМГ-6/0,4 кV 1 МВА ; ТМГ-10/0,4 кV 1 MBA | A total of 3 pcs. of 10 kV cells including: A relay protection and automation (RPA) panel with a microprocessor device and power direction - 1 pc. Vacuum switch 1 pc.; Surge arresters nonlinear - 3 pcs.; Current transformer -3 pcs; Power cables “КВВГЕнг 4*2,5” -0,45km ; “КВВГЕнг 10*2,5”-0,45km; “ПВ-1 2,5” - 0,6km
23 | 2000 | S3F Delta G-400 DN150 (1:160) min 4 max 650 | Gas metering cabinet | GPRC - 9/15 - 2L - 100x150 - 3/3 MBN-QA DN65х100 PN16 + OS/66-AP | Transformer substation consisting of: power transformer ТМГ-6/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs.; power cables “ААБл 10 3х240 mm2” 1,65 km; “ААБл 10 3х120 mm2” 2 km; Outdoor switchgear consisting of: vacuum switch cells - 5 pcs; voltage transformer cell - 1 pc.; Surge arresters nonlinear - 5 pcs.; | A total of 5 pcs. of 10 kV cells including: A relay protection and automation (RPA) panel with a microprocessor device and power direction - 1 pc. Vacuum switch 1 pc.; Surge arresters nonlinear - 3 pcs.; Current transformer -3 pcs; Power cables “КВВГЕнг 4*2,5” -0,75km ; “КВВГЕнг 10*2,5”-0,75km; “ПВ-1 2,5” - 1,0km
24 | 300 | G-65 Delta SE G-65 DN50 (1:200) min 0.5 max 100 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP | Power cables “ААБл 1 4х120 mm2” 0,2 km
25 | 700 | FLOWSIC500 G160 DN100 (1:50) min 5 max250 (Delta SE G-160 DN80 (1:200) min 1.3 max 250 G-160 there is no D100) | Gas metering cabinet | GPRC - 6/8 - 2L - 65x80 - 3/3 MBN-QA DN40х80 PN16 + OS/66-AP | Power cables “ААБл 1 4х120 mm2” 0,2 km; transformer substation consisting of: power transformer-10/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs.;
26 | 700 | FLOWSIC500 G160 DN100 (1:50) min 5 max250 (Delta SE G-160 DN80 (1:200) min 1.3 max 250 G-160 there is no D100) | Gas metering cabinet | GPRC - 6/8 - 2L - 65x80 - 3/3 MBN-QA DN40х80 PN16 + OS/66-AP | Power cables “ААБл 1 4х120 mm2” 0,2 km; transformer substation consisting of: power transformer-10/0,4 кV 630 КВА; high-voltage load switches - 3 pcs; panel equipment “ЩО-90” - 3 pcs.;
27 | 200 | Delta Compact G-40 DN50 (1:200) min 0,3 max 65 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP
28 | 200 | Delta Compact G-40 DN50 (1:200) min 0,3 max 65 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP
29 | 300 | G-65 Delta SE G-65 DN50 (1:200) min 0.5 max 100 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP
30 | 250 | G-65 Delta SE G-65 DN50 (1:200) min 0.5 max 100 | Gas metering cabinet | GPRC - 5/5 - 2L - 50x65 - 3/3 А/149-АР DN50 РN16 + OS/66- AP
31 | 70 | Delta Compact G16 DN50 (1:100) min 0,25 max 25 | Gas metering cabinet | GPRC - 2/2 - 2L - 25x32 - 3/3/74-AP 3/4"x1/4"
32 | 70 | Delta Compact G16 DN50 (1:100) min 0,25 max 25 | Gas metering cabinet | GPRC - 2/2 - 2L - 25x32 - 3/3/74-AP 3/4"x1/4"
33 | 70 | Delta Compact G16 DN50 (1:100) min 0,25 max 25 | Gas metering cabinet | GPRC - 2/2 - 2L - 25x32 - 3/3/74-AP 3/4"x1/4"
34 | 70 | Delta Compact G16 DN50 (1:100) min 0,25 max 25 | Gas metering cabinet | GPRC - 2/2 - 2L - 25x32 - 3/3/74-AP 3/4"x1/4"
35 | 70 | Delta Compact G16 DN50 (1:100) min 0,25 max 25 | Gas metering cabinet | GPRC - 2/2 - 2L - 25x32 - 3/3/74-AP 3/4"x1/4"
36 | 70 | Delta Compact G16 DN50 (1:100) min 0,25 max 25 | Gas metering cabinet | GPRC - 2/2 - 2L - 25x32 - 3/3/74-AP 3/4"x1/4"
37 | 70 | Delta Compact G16 DN50 (1:100) min 0,25 max 25 | Gas metering cabinet | GPRC - 2/2 - 2L - 25x32 - 3/3/74-AP 3/4"x1/4"
total | 57680
Note: References to a specific trade mark, firm, source of origin or manufacturer should read in conjunction with "or equivalent"