## Table 2
Gas turbine power units
Equipment of Municipal Enterprise “Kharkiv Heat Networks” |  |  | Equipment for connecting through gas distribution networks |  |  |  | Equipment for connecting through power distribution networks
No. | Electric capacity | Output voltage | Gas meter size* | Metering unit* | Gas pressure regulating cabinet (GPRC)* | Additional compressor unit | Energy equipment
1 | 54 MW | 11 кV | FLOWSIC600 G4000 DN300 (1:100) min 65 max 6500 - 2 pcs. per unit | Gas metering cabinet FLOWSIC600 - 2 pcs. per unit | Additional compressor unit and GPRC - 2L - 500x600 - 3/3 FL + MB5 DN250 PN16 + PS/79-2 + OS/80X-BPA are needed | Increase from 0.15 MPa to 0.6 MPa
2 | 40 MW | 11 кV | FLOWSIC600 G4000 DN300 (1:100) min 65 max 6500 - 2 pcs. per unit | Gas metering cabinet FLOWSIC600 - 2 pcs. per unit | Additional compressor unit and GPRC - 2L - 500x600 - 3/3 FL + MB5 DN250 PN16 + PS/79-2 + OS/80X-BPA are needed | Increase from 0.15 MPa to 0.6 MPa
3 | 40 MW | 11 кV | FLOWSIC600 G4000 DN300 (1:100) min 65 max 6500 - 2 pcs. per unit | Gas metering cabinet FLOWSIC600 - 2 pcs. per unit | Additional compressor unit and GPRC - 2L - 500x600 - 3/3 FL + MB5 DN250 PN16 + PS/79-2 + OS/80X-BPA are needed | Increase from 0.15 MPa to 0.6 MPa
4 | 40 MW | 11 кV | FLOWSIC600 G4000 DN300 (1:100) min 65 max 6500 - 2 pcs. per unit | Gas metering cabinet FLOWSIC600 - 2 pcs. per unit | Additional compressor unit and GPRC - 2L - 500x600 - 3/3 FL + MB5 DN250 PN16 + PS/79-2 + OS/80X-BPA are needed | Increase from 0.15 MPa to 0.6 MPa | A 110 kV cell including: 110 кV electric gas switch - 1 pc; 110 кV disconnector - 2 pcs.; Surge arresters nonlinear - 3 pcs.; 110 кV current transformer - 3 pcs.; A relay protection and automation (RPA) panel with a microprocessor device and power direction + alarm system - 1 pc.; backup protection panel - 1 pc; control panel - 1 pc; power cables “КВВГЕнг 4*2,5” - 2,5km; “КВВГЕнг 19*2,5”- 2km; “КВВГЕнг 10*2,5” - 2,5km; “КВВГЕнг 4*7” - 2km; “АС-240”-2km; blocking relay - 10 pcs.; cable trays - 200 pcs.; external man-machine devices - 10 pcs.; suspended insulation LK-110 kV-100 pcs.; line traps - 10 pcs.; accounting devices - 70 pcs.; terminal block (TM and TV)-31pcs; current-limiting reactors-6 pcs.; portal racks-8 pcs.; portal rack jumpers- 4 pcs.; line fittings -100v
Note: References to a specific trade mark, firm, source of origin or manufacturer should read in conjunction with "or equivalent"